## Inlet Flow
AMBIENT PRESSURE= |  | 14.696 | PSIA
AMBIENT TEMPERATURE= |  | 100 | DEG F
INLET PRESSURE= |  | 14.496 | PSIA
INLET TEMPERATURE= |  | 97.8041 | DEG F
FLUID DENSITY= |  | 0.070147 | LB/FT3
DIAM | FLOW | FLOW | FLOW | VELOCITY | VELOCITY | VELOCITY
(IN) | (SCFM) | (LB/MIN) | (ACFM) | (FPS) | (FPM) | (High/Low ?)
48 | 100000 | 7512.94 | 107102.2765 | 142.0488 | 8522.9284 | High
48 | 98000 | 7362.6812 | 104960.231 | 139.2078 | 8352.4698 | High
48 | 96000 | 7212.4224 | 102818.1855 | 136.3669 | 8182.0112 | High
48 | 94000 | 7062.1636 | 100676.1399 | 133.5259 | 8011.5527 | High
48 | 92000 | 6911.9048 | 98534.0944 | 130.6849 | 7841.0941 | High
48 | 90000 | 6761.646 | 96392.0489 | 127.8439 | 7670.6355 | High
48 | 88000 | 6611.3872 | 94250.0033 | 125.0029 | 7500.177 | High
48 | 86000 | 6461.1284 | 92107.9578 | 122.162 | 7329.7184 | High
48 | 84000 | 6310.8696 | 89965.9123 | 119.321 | 7159.2598 | High
48 | 82000 | 6160.6108 | 87823.8667 | 116.48 | 6988.8013 | High
48 | 80000 | 6010.352 | 85681.8212 | 113.639 | 6818.3427 | High
48 | 78000 | 5860.0932 | 83539.7757 | 110.7981 | 6647.8841 | High
48 | 76000 | 5709.8344 | 81397.7302 | 107.9571 | 6477.4256
48 | 74000 | 5559.5756 | 79255.6846 | 105.1161 | 6306.967
48 | 72000 | 5409.3168 | 77113.6391 | 102.2751 | 6136.5084
48 | 70000 | 5259.058 | 74971.5936 | 99.4342 | 5966.0499
48 | 68000 | 5108.7992 | 72829.548 | 96.5932 | 5795.5913
48 | 66000 | 4958.5404 | 70687.5025 | 93.7522 | 5625.1327
48 | 64000 | 4808.2816 | 68545.457 | 90.9112 | 5454.6742
48 | 62000 | 4658.0228 | 66403.4114 | 88.0703 | 5284.2156
48 | 60000 | 4507.764 | 64261.3659 | 85.2293 | 5113.757
48 | 58000 | 4357.5052 | 62119.3204 | 82.3883 | 4943.2984
48 | 56000 | 4207.2464 | 59977.2748 | 79.5473 | 4772.8399
48 | 54000 | 4056.9876 | 57835.2293 | 76.7064 | 4602.3813
48 | 52000 | 3906.7288 | 55693.1838 | 73.8654 | 4431.9227
48 | 50000 | 3756.47 | 53551.1383 | 71.0244 | 4261.4642
42 | 79862.1971 | 5999.999 | 85534.2312 | 148.1708 | 8890.2502 | High
42 | 79829.6966 | 5997.5572 | 85499.4224 | 148.1105 | 8886.6323 | High
42 | 79808.4597 | 5995.9617 | 85476.6772 | 148.0711 | 8884.2682 | High
42 | 74000 | 5559.5756 | 79255.6846 | 137.2945 | 8237.6712 | High
42 | 72000 | 5409.3168 | 77113.6391 | 133.5839 | 8015.0314 | High
42 | 70000 | 5259.058 | 74971.5936 | 129.8732 | 7792.3916 | High
42 | 68000 | 5108.7992 | 72829.548 | 126.1625 | 7569.7519 | High
42 | 66000 | 4958.5404 | 70687.5025 | 122.4519 | 7347.1121 | High
42 | 64000 | 4808.2816 | 68545.457 | 118.7412 | 7124.4724 | High
42 | 62000 | 4658.0228 | 66403.4114 | 115.0305 | 6901.8326 | High
42 | 60000 | 4507.764 | 64261.3659 | 111.3199 | 6679.1928 | High
42 | 58000 | 4357.5052 | 62119.3204 | 107.6092 | 6456.5531
42 | 56000 | 4207.2464 | 59977.2748 | 103.8986 | 6233.9133
42 | 54000 | 4056.9876 | 57835.2293 | 100.1879 | 6011.2736
42 | 52000 | 3906.7288 | 55693.1838 | 96.4772 | 5788.6338
42 | 50000 | 3756.47 | 53551.1383 | 92.7666 | 5565.994
42 | 48000 | 3606.2112 | 51409.0927 | 89.0559 | 5343.3543
42 | 46000 | 3455.9524 | 49267.0472 | 85.3452 | 5120.7145
42 | 44000 | 3305.6936 | 47125.0017 | 81.6346 | 4898.0747
42 | 42000 | 3155.4348 | 44982.9561 | 77.9239 | 4675.435
42 | 40000 | 3005.176 | 42840.9106 | 74.2133 | 4452.7952
36 | 60000 | 4507.764 | 64261.3659 | 151.5187 | 9091.1236 | High
36 | 58000 | 4357.5052 | 62119.3204 | 146.4681 | 8788.0861 | High
36 | 56000 | 4207.2464 | 59977.2748 | 141.4175 | 8485.0487 | High
36 | 54000 | 4056.9876 | 57835.2293 | 136.3669 | 8182.0112 | High
36 | 52000 | 3906.7288 | 55693.1838 | 131.3162 | 7878.9738 | High
36 | 50000 | 3756.47 | 53551.1383 | 126.2656 | 7575.9363 | High
36 | 48000 | 3606.2112 | 51409.0927 | 121.215 | 7272.8989 | High
36 | 46000 | 3455.9524 | 49267.0472 | 116.1644 | 6969.8614 | High
36 | 44000 | 3305.6936 | 47125.0017 | 111.1137 | 6666.824 | High
36 | 42000 | 3155.4348 | 44982.9561 | 106.0631 | 6363.7865
36 | 40000 | 3005.176 | 42840.9106 | 101.0125 | 6060.7491
36 | 38000 | 2854.9172 | 40698.8651 | 95.9619 | 5757.7116
36 | 36000 | 2704.6584 | 38556.8195 | 90.9112 | 5454.6742
36 | 34000 | 2554.3996 | 36414.774 | 85.8606 | 5151.6367
36 | 32000 | 2404.1408 | 34272.7285 | 80.81 | 4848.5992
36 | 30000 | 2253.882 | 32130.683 | 75.7594 | 4545.5618
30 | 40000 | 3005.176 | 42840.9106 | 145.458 | 8727.4786 | High
30 | 39000 | 2930.0466 | 41769.8878 | 141.8215 | 8509.2917 | High
30 | 38000 | 2854.9172 | 40698.8651 | 138.1851 | 8291.1047 | High
30 | 37000 | 2779.7878 | 39627.8423 | 134.5486 | 8072.9177 | High
30 | 36000 | 2704.6584 | 38556.8195 | 130.9122 | 7854.7308 | High
30 | 35000 | 2629.529 | 37485.7968 | 127.2757 | 7636.5438 | High
30 | 34000 | 2554.3996 | 36414.774 | 123.6393 | 7418.3568 | High
30 | 33000 | 2479.2702 | 35343.7512 | 120.0028 | 7200.1699 | High
30 | 32000 | 2404.1408 | 34272.7285 | 116.3664 | 6981.9829 | High
30 | 31000 | 2329.0114 | 33201.7057 | 112.7299 | 6763.7959 | High
30 | 30000 | 2253.882 | 32130.683 | 109.0935 | 6545.609 | High
30 | 29000 | 2178.7526 | 31059.6602 | 105.457 | 6327.422
30 | 28000 | 2103.6232 | 29988.6374 | 101.8206 | 6109.235
30 | 27000 | 2028.4938 | 28917.6147 | 98.1841 | 5891.0481
30 | 26000 | 1953.3644 | 27846.5919 | 94.5477 | 5672.8611
30 | 25000 | 1878.235 | 26775.5691 | 90.9112 | 5454.6742
30 | 24000 | 1803.1056 | 25704.5464 | 87.2748 | 5236.4872
30 | 23000 | 1727.9762 | 24633.5236 | 83.6383 | 5018.3002
30 | 22000 | 1652.8468 | 23562.5008 | 80.0019 | 4800.1133
30 | 21000 | 1577.7174 | 22491.4781 | 76.3654 | 4581.9263
30 | 20000 | 1502.588 | 21420.4553 | 72.729 | 4363.7393
24 | 16000 | 1202.0704 | 17136.3642 | 90.9112 | 5454.6742 | High
24 | 15500 | 1164.5057 | 16600.8529 | 88.0703 | 5284.2156 | High
24 | 15000 | 1126.941 | 16065.3415 | 85.2293 | 5113.757 | High
24 | 14500 | 1089.3763 | 15529.8301 | 82.3883 | 4943.2984 | High
24 | 14000 | 1051.8116 | 14994.3187 | 79.5473 | 4772.8399 | High
24 | 13500 | 1014.2469 | 14458.8073 | 76.7064 | 4602.3813 | High
24 | 13000 | 976.6822 | 13923.2959 | 73.8654 | 4431.9227 | High
24 | 12500 | 939.1175 | 13387.7846 | 71.0244 | 4261.4642 | High
24 | 12000 | 901.5528 | 12852.2732 | 68.1834 | 4091.0056 | High
24 | 11500 | 863.9881 | 12316.7618 | 65.3425 | 3920.547
24 | 11000 | 826.4234 | 11781.2504 | 62.5015 | 3750.0885
24 | 10500 | 788.8587 | 11245.739 | 59.6605 | 3579.6299
24 | 10000 | 751.294 | 10710.2277 | 56.8195 | 3409.1713
20 | 11000 | 826.4234 | 11781.2504 | 90.0021 | 5400.1274 | High
20 | 10800 | 811.3975 | 11567.0459 | 88.3657 | 5301.9433 | High
20 | 10600 | 796.3716 | 11352.8413 | 86.7293 | 5203.7591 | High
20 | 10400 | 781.3458 | 11138.6368 | 85.0929 | 5105.575 | High
20 | 10200 | 766.3199 | 10924.4322 | 83.4565 | 5007.3909 | High
20 | 10000 | 751.294 | 10710.2277 | 81.8201 | 4909.2067 | High
20 | 9800 | 736.2681 | 10496.0231 | 80.1837 | 4811.0226 | High
20 | 9600 | 721.2422 | 10281.8185 | 78.5473 | 4712.8385 | High
20 | 9400 | 706.2164 | 10067.614 | 76.9109 | 4614.6543 | High
20 | 9200 | 691.1905 | 9853.4094 | 75.2745 | 4516.4702 | High
20 | 9000 | 676.1646 | 9639.2049 | 73.6381 | 4418.2861 | High
20 | 8800 | 661.1387 | 9425.0003 | 72.0017 | 4320.1019 | High
20 | 8600 | 646.1128 | 9210.7958 | 70.3653 | 4221.9178 | High
20 | 8400 | 631.087 | 8996.5912 | 68.7289 | 4123.7337 | High
20 | 8200 | 616.0611 | 8782.3867 | 67.0925 | 4025.5495 | High
20 | 8000 | 601.0352 | 8568.1821 | 65.4561 | 3927.3654
20 | 7800 | 586.0093 | 8353.9776 | 63.8197 | 3829.1813
20 | 7600 | 570.9834 | 8139.773 | 62.1833 | 3730.9971
20 | 7400 | 555.9576 | 7925.5685 | 60.5469 | 3632.813
20 | 7200 | 540.9317 | 7711.3639 | 58.9105 | 3534.6289
20 | 7000 | 525.9058 | 7497.1594 | 57.2741 | 3436.4447
18 | 9000 | 676.1646 | 9639.2049 | 90.9112 | 5454.6742 | High
18 | 8800 | 661.1387 | 9425.0003 | 88.891 | 5333.4592 | High
18 | 8600 | 646.1128 | 9210.7958 | 86.8707 | 5212.2442 | High
18 | 8400 | 631.087 | 8996.5912 | 84.8505 | 5091.0292 | High
18 | 8200 | 616.0611 | 8782.3867 | 82.8302 | 4969.8142 | High
18 | 8000 | 601.0352 | 8568.1821 | 80.81 | 4848.5992 | High
18 | 7800 | 586.0093 | 8353.9776 | 78.7897 | 4727.3843 | High
18 | 7600 | 570.9834 | 8139.773 | 76.7695 | 4606.1693 | High
18 | 7400 | 555.9576 | 7925.5685 | 74.7492 | 4484.9543 | High
18 | 7200 | 540.9317 | 7711.3639 | 72.729 | 4363.7393 | High
18 | 7000 | 525.9058 | 7497.1594 | 70.7087 | 4242.5243 | High
18 | 6800 | 510.8799 | 7282.9548 | 68.6885 | 4121.3094 | High
18 | 6600 | 495.854 | 7068.7502 | 66.6682 | 4000.0944 | High
18 | 6400 | 480.8282 | 6854.5457 | 64.648 | 3878.8794
18 | 6200 | 465.8023 | 6640.3411 | 62.6277 | 3757.6644
18 | 6000 | 450.7764 | 6426.1366 | 60.6075 | 3636.4494
16 | 7000 | 525.9058 | 7497.1594 | 89.4907 | 5369.4449 | High
16 | 6800 | 510.8799 | 7282.9548 | 86.9339 | 5216.0322 | High
16 | 6600 | 495.854 | 7068.7502 | 84.377 | 5062.6194 | High
16 | 6400 | 480.8282 | 6854.5457 | 81.8201 | 4909.2067 | High
16 | 6200 | 465.8023 | 6640.3411 | 79.2632 | 4755.794 | High
16 | 6000 | 450.7764 | 6426.1366 | 76.7064 | 4602.3813 | High
16 | 5800 | 435.7505 | 6211.932 | 74.1495 | 4448.9686 | High
16 | 5600 | 420.7246 | 5997.7275 | 71.5926 | 4295.5559 | High
16 | 5400 | 405.6988 | 5783.5229 | 69.0357 | 4142.1432 | High
16 | 5200 | 390.6729 | 5569.3184 | 66.4788 | 3988.7305
16 | 5000 | 375.647 | 5355.1138 | 63.922 | 3835.3178
16 | 4800 | 360.6211 | 5140.9093 | 61.3651 | 3681.9051
16 | 4600 | 345.5952 | 4926.7047 | 58.8082 | 3528.4923
16 | 4400 | 330.5694 | 4712.5002 | 56.2513 | 3375.0796
14 | 5500 | 413.2117 | 5890.6252 | 91.8389 | 5510.3341 | High
14 | 5300 | 398.1858 | 5676.4207 | 88.4993 | 5309.9583 | High
14 | 5100 | 383.1599 | 5462.2161 | 85.1597 | 5109.5825 | High
14 | 4900 | 368.1341 | 5248.0115 | 81.8201 | 4909.2067 | High
14 | 4700 | 353.1082 | 5033.807 | 78.4805 | 4708.831 | High
14 | 4500 | 338.0823 | 4819.6024 | 75.1409 | 4508.4552 | High
14 | 4300 | 323.0564 | 4605.3979 | 71.8013 | 4308.0794 | High
14 | 4100 | 308.0305 | 4391.1933 | 68.4617 | 4107.7036 | High
14 | 3900 | 293.0047 | 4176.9888 | 65.1221 | 3907.3278
14 | 3700 | 277.9788 | 3962.7842 | 61.7825 | 3706.952
14 | 3500 | 262.9529 | 3748.5797 | 58.4429 | 3506.5762
12 | 4000 | 300.5176 | 4284.0911 | 90.9112 | 5454.6742 | High
12 | 3900 | 293.0047 | 4176.9888 | 88.6385 | 5318.3073 | High
12 | 3800 | 285.4917 | 4069.8865 | 86.3657 | 5181.9404 | High
12 | 3700 | 277.9788 | 3962.7842 | 84.0929 | 5045.5736 | High
12 | 3600 | 270.4658 | 3855.682 | 81.8201 | 4909.2067 | High
12 | 3500 | 262.9529 | 3748.5797 | 79.5473 | 4772.8399 | High
12 | 3400 | 255.44 | 3641.4774 | 77.2746 | 4636.473 | High
12 | 3300 | 247.927 | 3534.3751 | 75.0018 | 4500.1062 | High
12 | 3200 | 240.4141 | 3427.2728 | 72.729 | 4363.7393 | High
12 | 3100 | 232.9011 | 3320.1706 | 70.4562 | 4227.3725 | High
12 | 3000 | 225.3882 | 3213.0683 | 68.1834 | 4091.0056 | High
12 | 2900 | 217.8753 | 3105.966 | 65.9106 | 3954.6388
12 | 2800 | 210.3623 | 2998.8637 | 63.6379 | 3818.2719
12 | 2700 | 202.8494 | 2891.7615 | 61.3651 | 3681.9051
12 | 2600 | 195.3364 | 2784.6592 | 59.0923 | 3545.5382
12 | 2500 | 187.8235 | 2677.5569 | 56.8195 | 3409.1713
10 | 2100 | 157.7717 | 2249.1478 | 68.7289 | 4123.7337 | High
10 | 2050 | 154.0153 | 2195.5967 | 67.0925 | 4025.5495 | High
10 | 2000 | 150.2588 | 2142.0455 | 65.4561 | 3927.3654 | High
10 | 1950 | 146.5023 | 2088.4944 | 63.8197 | 3829.1813 | High
10 | 1900 | 142.7459 | 2034.9433 | 62.1833 | 3730.9971 | High
10 | 1850 | 138.9894 | 1981.3921 | 60.5469 | 3632.813 | High
10 | 1800 | 135.2329 | 1927.841 | 58.9105 | 3534.6289 | High
10 | 1750 | 131.4764 | 1874.2898 | 57.2741 | 3436.4447 | High
10 | 1700 | 127.72 | 1820.7387 | 55.6377 | 3338.2606 | High
10 | 1650 | 123.9635 | 1767.1876 | 54.0013 | 3240.0764 | High
10 | 1600 | 120.207 | 1713.6364 | 52.3649 | 3141.8923 | High
10 | 1550 | 116.4506 | 1660.0853 | 50.7285 | 3043.7082 | High
10 | 1500 | 112.6941 | 1606.5341 | 49.0921 | 2945.524
10 | 1450 | 108.9376 | 1552.983 | 47.4557 | 2847.3399
10 | 1400 | 105.1812 | 1499.4319 | 45.8193 | 2749.1558
10 | 1350 | 101.4247 | 1445.8807 | 44.1829 | 2650.9716
10 | 1300 | 97.6682 | 1392.3296 | 42.5465 | 2552.7875
10 | 1250 | 93.9117 | 1338.7785 | 40.9101 | 2454.6034
10 | 1200 | 90.1553 | 1285.2273 | 39.2737 | 2356.4192
8 | 1350 | 101.4247 | 1445.8807 | 69.0357 | 4142.1432 | High
8 | 1300 | 97.6682 | 1392.3296 | 66.4788 | 3988.7305 | High
8 | 1250 | 93.9117 | 1338.7785 | 63.922 | 3835.3178 | High
8 | 1200 | 90.1553 | 1285.2273 | 61.3651 | 3681.9051 | High
8 | 1150 | 86.3988 | 1231.6762 | 58.8082 | 3528.4923 | High
8 | 1100 | 82.6423 | 1178.125 | 56.2513 | 3375.0796 | High
8 | 1050 | 78.8859 | 1124.5739 | 53.6944 | 3221.6669 | High
8 | 1000 | 75.1294 | 1071.0228 | 51.1376 | 3068.2542 | High
8 | 950 | 71.3729 | 1017.4716 | 48.5807 | 2914.8415
8 | 900 | 67.6165 | 963.9205 | 46.0238 | 2761.4288
8 | 850 | 63.86 | 910.3694 | 43.4669 | 2608.0161
8 | 800 | 60.1035 | 856.8182 | 40.9101 | 2454.6034
8 | 750 | 56.347 | 803.2671 | 38.3532 | 2301.1907
8 | 700 | 52.5906 | 749.7159 | 35.7963 | 2147.7779
6 | 750 | 56.347 | 803.2671 | 68.1834 | 4091.0056 | High
6 | 700 | 52.5906 | 749.7159 | 63.6379 | 3818.2719 | High
6 | 650 | 48.8341 | 696.1648 | 59.0923 | 3545.5382 | High
6 | 600 | 45.0776 | 642.6137 | 54.5467 | 3272.8045 | High
6 | 550 | 41.3212 | 589.0625 | 50.0012 | 3000.0708 | High
6 | 500 | 37.5647 | 535.5114 | 45.4556 | 2727.3371
6 | 450 | 33.8082 | 481.9602 | 40.9101 | 2454.6034
6 | 400 | 30.0518 | 428.4091 | 36.3645 | 2181.8697
6 | 350 | 26.2953 | 374.858 | 31.8189 | 1909.136
6 | 300 | 22.5388 | 321.3068 | 27.2734 | 1636.4022 | Low
4 | 350 | 26.2953 | 374.858 | 71.5926 | 4295.5559 | High
4 | 340 | 25.544 | 364.1477 | 69.5471 | 4172.8257 | High
4 | 330 | 24.7927 | 353.4375 | 67.5016 | 4050.0956 | High
4 | 320 | 24.0414 | 342.7273 | 65.4561 | 3927.3654 | High
4 | 310 | 23.2901 | 332.0171 | 63.4106 | 3804.6352 | High
4 | 300 | 22.5388 | 321.3068 | 61.3651 | 3681.9051 | High
4 | 290 | 21.7875 | 310.5966 | 59.3196 | 3559.1749 | High
4 | 280 | 21.0362 | 299.8864 | 57.2741 | 3436.4447 | High
4 | 270 | 20.2849 | 289.1761 | 55.2286 | 3313.7145 | High
4 | 260 | 19.5336 | 278.4659 | 53.1831 | 3190.9844 | High
4 | 250 | 18.7824 | 267.7557 | 51.1376 | 3068.2542 | High
4 | 240 | 18.0311 | 257.0455 | 49.0921 | 2945.524
4 | 230 | 17.2798 | 246.3352 | 47.0466 | 2822.7939
4 | 220 | 16.5285 | 235.625 | 45.0011 | 2700.0637
4 | 210 | 15.7772 | 224.9148 | 42.9556 | 2577.3335
4 | 200 | 15.0259 | 214.2046 | 40.9101 | 2454.6034
4 | 190 | 14.2746 | 203.4943 | 38.8646 | 2331.8732
4 | 180 | 13.5233 | 192.7841 | 36.8191 | 2209.143
Note on G7: Hiran de Mel: The vast majority of systems utilizing centrifugal blowers are designed at pipe velocities of less than 3500 FPM which minimizes line losses and noise, with an accompanying decrease in power consumption.

## Discharge Flow
INLET PRESSURE = |  | 14.496 | PSIA
INLET TEMPERATURE = |  | 97.8041 | DEG F
FLUID PRESSURE = |  | 34.5 | PSIA
FLUID TEMPERATURE = |  | 360.2033 | DEG F
FLUID DENSITY = |  | 0.11354 | LB/FT3
DIAM | FLOW | FLOW | FLOW | VELOCITY | VELOCITY | VELOCITY
(IN) | (SCFM) | (LB/MIN) | (ACFM) | (FPS) | (FPM) | (High/Low ?)
48 | 100000 | 7512.94 | 66170.9798 | 87.762 | 5265.7193
48 | 98000 | 7362.6812 | 64847.5602 | 86.0067 | 5160.4049
48 | 96000 | 7212.4224 | 63524.1406 | 84.2515 | 5055.0905
48 | 94000 | 7062.1636 | 62200.721 | 82.4963 | 4949.7761
48 | 92000 | 6911.9048 | 60877.3014 | 80.741 | 4844.4617
48 | 90000 | 6761.646 | 59553.8818 | 78.9858 | 4739.1473
48 | 88000 | 6611.3872 | 58230.4622 | 77.2305 | 4633.8329
48 | 86000 | 6461.1284 | 56907.0426 | 75.4753 | 4528.5186
48 | 84000 | 6310.8696 | 55583.623 | 73.7201 | 4423.2042
48 | 82000 | 6160.6108 | 54260.2034 | 71.9648 | 4317.8898
48 | 80000 | 6010.352 | 52936.7838 | 70.2096 | 4212.5754
48 | 78000 | 5860.0932 | 51613.3642 | 68.4544 | 4107.261
48 | 76000 | 5709.8344 | 50289.9446 | 66.6991 | 4001.9466
48 | 74000 | 5559.5756 | 48966.525 | 64.9439 | 3896.6323
48 | 72000 | 5409.3168 | 47643.1054 | 63.1886 | 3791.3179 | Low
48 | 70000 | 5259.058 | 46319.6858 | 61.4334 | 3686.0035 | Low
48 | 68000 | 5108.7992 | 44996.2662 | 59.6782 | 3580.6891 | Low
48 | 66000 | 4958.5404 | 43672.8466 | 57.9229 | 3475.3747 | Low
48 | 64000 | 4808.2816 | 42349.427 | 56.1677 | 3370.0603 | Low
48 | 62000 | 4658.0228 | 41026.0074 | 54.4124 | 3264.7459 | Low
48 | 60000 | 4507.764 | 39702.5879 | 52.6572 | 3159.4316 | Low
48 | 58000 | 4357.5052 | 38379.1683 | 50.902 | 3054.1172 | Low
48 | 56000 | 4207.2464 | 37055.7487 | 49.1467 | 2948.8028 | Low
48 | 54000 | 4056.9876 | 35732.3291 | 47.3915 | 2843.4884 | Low
48 | 52000 | 3906.7288 | 34408.9095 | 45.6362 | 2738.174 | Low
48 | 50000 | 3756.47 | 33085.4899 | 43.881 | 2632.8596 | Low
42 | 80000 | 6010.352 | 52936.7838 | 91.7023 | 5502.1393
42 | 78000 | 5860.0932 | 51613.3642 | 89.4098 | 5364.5858
42 | 76000 | 5709.8344 | 50289.9446 | 87.1172 | 5227.0323
42 | 74000 | 5559.5756 | 48966.525 | 84.8246 | 5089.4789
42 | 72000 | 5409.3168 | 47643.1054 | 82.5321 | 4951.9254
42 | 70000 | 5259.058 | 46319.6858 | 80.2395 | 4814.3719
42 | 68000 | 5108.7992 | 44996.2662 | 77.947 | 4676.8184
42 | 66000 | 4958.5404 | 43672.8466 | 75.6544 | 4539.2649
42 | 64000 | 4808.2816 | 42349.427 | 73.3619 | 4401.7114
42 | 62000 | 4658.0228 | 41026.0074 | 71.0693 | 4264.158
42 | 60000 | 4507.764 | 39702.5879 | 68.7767 | 4126.6045
42 | 58000 | 4357.5052 | 38379.1683 | 66.4842 | 3989.051
42 | 56000 | 4207.2464 | 37055.7487 | 64.1916 | 3851.4975
42 | 54000 | 4056.9876 | 35732.3291 | 61.8991 | 3713.944 | Low
42 | 52000 | 3906.7288 | 34408.9095 | 59.6065 | 3576.3905 | Low
42 | 50000 | 3756.47 | 33085.4899 | 57.314 | 3438.8371 | Low
42 | 48000 | 3606.2112 | 31762.0703 | 55.0214 | 3301.2836 | Low
42 | 46000 | 3455.9524 | 30438.6507 | 52.7288 | 3163.7301 | Low
42 | 44000 | 3305.6936 | 29115.2311 | 50.4363 | 3026.1766 | Low
42 | 42000 | 3155.4348 | 27791.8115 | 48.1437 | 2888.6231 | Low
42 | 40000 | 3005.176 | 26468.3919 | 45.8512 | 2751.0697 | Low
36 | 60000 | 4507.764 | 39702.5879 | 93.6128 | 5616.7672
36 | 58000 | 4357.5052 | 38379.1683 | 90.4924 | 5429.5416
36 | 56000 | 4207.2464 | 37055.7487 | 87.3719 | 5242.3161
36 | 54000 | 4056.9876 | 35732.3291 | 84.2515 | 5055.0905
36 | 52000 | 3906.7288 | 34408.9095 | 81.1311 | 4867.8649
36 | 50000 | 3756.47 | 33085.4899 | 78.0107 | 4680.6393
36 | 48000 | 3606.2112 | 31762.0703 | 74.8902 | 4493.4138
36 | 46000 | 3455.9524 | 30438.6507 | 71.7698 | 4306.1882
36 | 44000 | 3305.6936 | 29115.2311 | 68.6494 | 4118.9626
36 | 42000 | 3155.4348 | 27791.8115 | 65.529 | 3931.737
36 | 40000 | 3005.176 | 26468.3919 | 62.4085 | 3744.5115 | Low
36 | 38000 | 2854.9172 | 25144.9723 | 59.2881 | 3557.2859 | Low
36 | 36000 | 2704.6584 | 23821.5527 | 56.1677 | 3370.0603 | Low
36 | 34000 | 2554.3996 | 22498.1331 | 53.0472 | 3182.8348 | Low
36 | 32000 | 2404.1408 | 21174.7135 | 49.9268 | 2995.6092 | Low
36 | 30000 | 2253.882 | 19851.2939 | 46.8064 | 2808.3836 | Low
30 | 40000 | 3005.176 | 26468.3919 | 89.8683 | 5392.0965
30 | 39000 | 2930.0466 | 25806.6821 | 87.6216 | 5257.2941
30 | 38000 | 2854.9172 | 25144.9723 | 85.3749 | 5122.4917
30 | 37000 | 2779.7878 | 24483.2625 | 83.1282 | 4987.6893
30 | 36000 | 2704.6584 | 23821.5527 | 80.8814 | 4852.8869
30 | 35000 | 2629.529 | 23159.8429 | 78.6347 | 4718.0845
30 | 34000 | 2554.3996 | 22498.1331 | 76.388 | 4583.282
30 | 33000 | 2479.2702 | 21836.4233 | 74.1413 | 4448.4796
30 | 32000 | 2404.1408 | 21174.7135 | 71.8946 | 4313.6772
30 | 31000 | 2329.0114 | 20513.0037 | 69.6479 | 4178.8748
30 | 30000 | 2253.882 | 19851.2939 | 67.4012 | 4044.0724
30 | 29000 | 2178.7526 | 19189.5841 | 65.1545 | 3909.27
30 | 28000 | 2103.6232 | 18527.8743 | 62.9078 | 3774.4676 | Low
30 | 27000 | 2028.4938 | 17866.1645 | 60.6611 | 3639.6652 | Low
30 | 26000 | 1953.3644 | 17204.4547 | 58.4144 | 3504.8627 | Low
30 | 25000 | 1878.235 | 16542.7449 | 56.1677 | 3370.0603 | Low
30 | 24000 | 1803.1056 | 15881.0351 | 53.921 | 3235.2579 | Low
30 | 23000 | 1727.9762 | 15219.3253 | 51.6743 | 3100.4555 | Low
30 | 22000 | 1652.8468 | 14557.6155 | 49.4276 | 2965.6531 | Low
30 | 21000 | 1577.7174 | 13895.9057 | 47.1808 | 2830.8507 | Low
30 | 20000 | 1502.588 | 13234.196 | 44.9341 | 2696.0483 | Low
24 | 16000 | 1202.0704 | 10587.3568 | 56.1677 | 3370.0603
24 | 15500 | 1164.5057 | 10256.5019 | 54.4124 | 3264.7459
24 | 15000 | 1126.941 | 9925.647 | 52.6572 | 3159.4316
24 | 14500 | 1089.3763 | 9594.7921 | 50.902 | 3054.1172
24 | 14000 | 1051.8116 | 9263.9372 | 49.1467 | 2948.8028
24 | 13500 | 1014.2469 | 8933.0823 | 47.3915 | 2843.4884
24 | 13000 | 976.6822 | 8602.2274 | 45.6362 | 2738.174
24 | 12500 | 939.1175 | 8271.3725 | 43.881 | 2632.8596 | Low
24 | 12000 | 901.5528 | 7940.5176 | 42.1258 | 2527.5452 | Low
24 | 11500 | 863.9881 | 7609.6627 | 40.3705 | 2422.2309 | Low
24 | 11000 | 826.4234 | 7278.8078 | 38.6153 | 2316.9165 | Low
24 | 10500 | 788.8587 | 6947.9529 | 36.86 | 2211.6021 | Low
24 | 10000 | 751.294 | 6617.098 | 35.1048 | 2106.2877 | Low
20 | 11000 | 826.4234 | 7278.8078 | 55.606 | 3336.3597
20 | 10800 | 811.3975 | 7146.4658 | 54.595 | 3275.6986
20 | 10600 | 796.3716 | 7014.1239 | 53.584 | 3215.0376
20 | 10400 | 781.3458 | 6881.7819 | 52.5729 | 3154.3765
20 | 10200 | 766.3199 | 6749.4399 | 51.5619 | 3093.7154
20 | 10000 | 751.294 | 6617.098 | 50.5509 | 3033.0543
20 | 9800 | 736.2681 | 6484.756 | 49.5399 | 2972.3932
20 | 9600 | 721.2422 | 6352.4141 | 48.5289 | 2911.7321
20 | 9400 | 706.2164 | 6220.0721 | 47.5179 | 2851.071
20 | 9200 | 691.1905 | 6087.7301 | 46.5068 | 2790.4099
20 | 9000 | 676.1646 | 5955.3882 | 45.4958 | 2729.7489
20 | 8800 | 661.1387 | 5823.0462 | 44.4848 | 2669.0878 | Low
20 | 8600 | 646.1128 | 5690.7043 | 43.4738 | 2608.4267 | Low
20 | 8400 | 631.087 | 5558.3623 | 42.4628 | 2547.7656 | Low
20 | 8200 | 616.0611 | 5426.0203 | 41.4517 | 2487.1045 | Low
20 | 8000 | 601.0352 | 5293.6784 | 40.4407 | 2426.4434 | Low
20 | 7800 | 586.0093 | 5161.3364 | 39.4297 | 2365.7823 | Low
20 | 7600 | 570.9834 | 5028.9945 | 38.4187 | 2305.1213 | Low
20 | 7400 | 555.9576 | 4896.6525 | 37.4077 | 2244.4602 | Low
20 | 7200 | 540.9317 | 4764.3105 | 36.3967 | 2183.7991 | Low
20 | 7000 | 525.9058 | 4631.9686 | 35.3856 | 2123.138 | Low
18 | 9000 | 676.1646 | 5955.3882 | 56.1677 | 3370.0603
18 | 8800 | 661.1387 | 5823.0462 | 54.9195 | 3295.1701
18 | 8600 | 646.1128 | 5690.7043 | 53.6713 | 3220.2799
18 | 8400 | 631.087 | 5558.3623 | 52.4232 | 3145.3896
18 | 8200 | 616.0611 | 5426.0203 | 51.175 | 3070.4994
18 | 8000 | 601.0352 | 5293.6784 | 49.9268 | 2995.6092
18 | 7800 | 586.0093 | 5161.3364 | 48.6786 | 2920.7189
18 | 7600 | 570.9834 | 5028.9945 | 47.4305 | 2845.8287
18 | 7400 | 555.9576 | 4896.6525 | 46.1823 | 2770.9385
18 | 7200 | 540.9317 | 4764.3105 | 44.9341 | 2696.0483 | Low
18 | 7000 | 525.9058 | 4631.9686 | 43.686 | 2621.158 | Low
18 | 6800 | 510.8799 | 4499.6266 | 42.4378 | 2546.2678 | Low
18 | 6600 | 495.854 | 4367.2847 | 41.1896 | 2471.3776 | Low
18 | 6400 | 480.8282 | 4234.9427 | 39.9415 | 2396.4873 | Low
18 | 6200 | 465.8023 | 4102.6007 | 38.6933 | 2321.5971 | Low
18 | 6000 | 450.7764 | 3970.2588 | 37.4451 | 2246.7069 | Low
16 | 7000 | 525.9058 | 4631.9686 | 55.2901 | 3317.4031
16 | 6800 | 510.8799 | 4499.6266 | 53.7103 | 3222.6202
16 | 6600 | 495.854 | 4367.2847 | 52.1306 | 3127.8372
16 | 6400 | 480.8282 | 4234.9427 | 50.5509 | 3033.0543
16 | 6200 | 465.8023 | 4102.6007 | 48.9712 | 2938.2713
16 | 6000 | 450.7764 | 3970.2588 | 47.3915 | 2843.4884
16 | 5800 | 435.7505 | 3837.9168 | 45.8118 | 2748.7055
16 | 5600 | 420.7246 | 3705.5749 | 44.232 | 2653.9225 | Low
16 | 5400 | 405.6988 | 3573.2329 | 42.6523 | 2559.1396 | Low
16 | 5200 | 390.6729 | 3440.8909 | 41.0726 | 2464.3566 | Low
16 | 5000 | 375.647 | 3308.549 | 39.4929 | 2369.5737 | Low
16 | 4800 | 360.6211 | 3176.207 | 37.9132 | 2274.7907 | Low
16 | 4600 | 345.5952 | 3043.8651 | 36.3335 | 2180.0078 | Low
16 | 4400 | 330.5694 | 2911.5231 | 34.7537 | 2085.2248 | Low
14 | 5500 | 413.2117 | 3639.4039 | 56.7408 | 3404.4487
14 | 5300 | 398.1858 | 3507.0619 | 54.6775 | 3280.6506
14 | 5100 | 383.1599 | 3374.72 | 52.6142 | 3156.8524
14 | 4900 | 368.1341 | 3242.378 | 50.5509 | 3033.0543
14 | 4700 | 353.1082 | 3110.036 | 48.4876 | 2909.2562
14 | 4500 | 338.0823 | 2977.6941 | 46.4243 | 2785.458
14 | 4300 | 323.0564 | 2845.3521 | 44.361 | 2661.6599 | Low
14 | 4100 | 308.0305 | 2713.0102 | 42.2977 | 2537.8618 | Low
14 | 3900 | 293.0047 | 2580.6682 | 40.2344 | 2414.0636 | Low
14 | 3700 | 277.9788 | 2448.3263 | 38.1711 | 2290.2655 | Low
14 | 3500 | 262.9529 | 2315.9843 | 36.1078 | 2166.4674 | Low
12 | 4000 | 300.5176 | 2646.8392 | 56.1677 | 3370.0603
12 | 3900 | 293.0047 | 2580.6682 | 54.7635 | 3285.8088
12 | 3800 | 285.4917 | 2514.4972 | 53.3593 | 3201.5573
12 | 3700 | 277.9788 | 2448.3263 | 51.9551 | 3117.3058
12 | 3600 | 270.4658 | 2382.1553 | 50.5509 | 3033.0543
12 | 3500 | 262.9529 | 2315.9843 | 49.1467 | 2948.8028
12 | 3400 | 255.44 | 2249.8133 | 47.7425 | 2864.5513
12 | 3300 | 247.927 | 2183.6423 | 46.3383 | 2780.2998
12 | 3200 | 240.4141 | 2117.4714 | 44.9341 | 2696.0483 | Low
12 | 3100 | 232.9011 | 2051.3004 | 43.5299 | 2611.7968 | Low
12 | 3000 | 225.3882 | 1985.1294 | 42.1258 | 2527.5452 | Low
12 | 2900 | 217.8753 | 1918.9584 | 40.7216 | 2443.2937 | Low
12 | 2800 | 210.3623 | 1852.7874 | 39.3174 | 2359.0422 | Low
12 | 2700 | 202.8494 | 1786.6165 | 37.9132 | 2274.7907 | Low
12 | 2600 | 195.3364 | 1720.4455 | 36.509 | 2190.5392 | Low
12 | 2500 | 187.8235 | 1654.2745 | 35.1048 | 2106.2877 | Low
10 | 3500 | 262.9529 | 2315.9843 | 70.7713 | 4246.276 | High
10 | 2200 | 165.2847 | 1455.7616 | 44.4848 | 2669.0878
10 | 2000 | 150.2588 | 1323.4196 | 40.4407 | 2426.4434
10 | 1950 | 146.5023 | 1290.3341 | 39.4297 | 2365.7823
10 | 1900 | 142.7459 | 1257.2486 | 38.4187 | 2305.1213
10 | 1850 | 138.9894 | 1224.1631 | 37.4077 | 2244.4602
10 | 1800 | 135.2329 | 1191.0776 | 36.3967 | 2183.7991
10 | 1750 | 131.4764 | 1157.9921 | 35.3856 | 2123.138
10 | 1700 | 127.72 | 1124.9067 | 34.3746 | 2062.4769
10 | 1650 | 123.9635 | 1091.8212 | 33.3636 | 2001.8158
10 | 1600 | 120.207 | 1058.7357 | 32.3526 | 1941.1547
10 | 1550 | 116.4506 | 1025.6502 | 31.3416 | 1880.4937
10 | 1500 | 112.6941 | 992.5647 | 30.3305 | 1819.8326
10 | 1450 | 108.9376 | 959.4792 | 29.3195 | 1759.1715 | Low
10 | 1400 | 105.1812 | 926.3937 | 28.3085 | 1698.5104 | Low
10 | 1350 | 101.4247 | 893.3082 | 27.2975 | 1637.8493 | Low
10 | 1300 | 97.6682 | 860.2227 | 26.2865 | 1577.1882 | Low
10 | 1250 | 93.9117 | 827.1372 | 25.2755 | 1516.5271 | Low
10 | 1200 | 90.1553 | 794.0518 | 24.2644 | 1455.8661 | Low
8 | 1350 | 101.4247 | 893.3082 | 42.6523 | 2559.1396
8 | 1300 | 97.6682 | 860.2227 | 41.0726 | 2464.3566
8 | 1250 | 93.9117 | 827.1372 | 39.4929 | 2369.5737
8 | 1200 | 90.1553 | 794.0518 | 37.9132 | 2274.7907
8 | 1150 | 86.3988 | 760.9663 | 36.3335 | 2180.0078
8 | 1100 | 82.6423 | 727.8808 | 34.7537 | 2085.2248
8 | 1050 | 78.8859 | 694.7953 | 33.174 | 1990.4419
8 | 1000 | 75.1294 | 661.7098 | 31.5943 | 1895.6589
8 | 950 | 71.3729 | 628.6243 | 30.0146 | 1800.876
8 | 900 | 67.6165 | 595.5388 | 28.4349 | 1706.093 | Low
8 | 850 | 63.86 | 562.4533 | 26.8552 | 1611.3101 | Low
8 | 800 | 60.1035 | 529.3678 | 25.2755 | 1516.5271 | Low
8 | 750 | 56.347 | 496.2823 | 23.6957 | 1421.7442 | Low
8 | 700 | 52.5906 | 463.1969 | 22.116 | 1326.9613 | Low
6 | 750 | 56.347 | 496.2823 | 42.1258 | 2527.5452
6 | 700 | 52.5906 | 463.1969 | 39.3174 | 2359.0422
6 | 650 | 48.8341 | 430.1114 | 36.509 | 2190.5392
6 | 600 | 45.0776 | 397.0259 | 33.7006 | 2022.0362
6 | 550 | 41.3212 | 363.9404 | 30.8922 | 1853.5332
6 | 500 | 37.5647 | 330.8549 | 28.0838 | 1685.0302 | Low
6 | 450 | 33.8082 | 297.7694 | 25.2755 | 1516.5271 | Low
6 | 400 | 30.0518 | 264.6839 | 22.4671 | 1348.0241 | Low
6 | 350 | 26.2953 | 231.5984 | 19.6587 | 1179.5211 | Low
6 | 300 | 22.5388 | 198.5129 | 16.8503 | 1011.0181 | Low
4 | 350 | 26.2953 | 231.5984 | 44.232 | 2653.9225
4 | 340 | 25.544 | 224.9813 | 42.9683 | 2578.0961
4 | 330 | 24.7927 | 218.3642 | 41.7045 | 2502.2698
4 | 320 | 24.0414 | 211.7471 | 40.4407 | 2426.4434
4 | 310 | 23.2901 | 205.13 | 39.177 | 2350.6171
4 | 300 | 22.5388 | 198.5129 | 37.9132 | 2274.7907
4 | 290 | 21.7875 | 191.8958 | 36.6494 | 2198.9644
4 | 280 | 21.0362 | 185.2787 | 35.3856 | 2123.138
4 | 270 | 20.2849 | 178.6616 | 34.1219 | 2047.3116
4 | 260 | 19.5336 | 172.0445 | 32.8581 | 1971.4853
4 | 250 | 18.7824 | 165.4274 | 31.5943 | 1895.6589
4 | 240 | 18.0311 | 158.8104 | 30.3305 | 1819.8326
4 | 230 | 17.2798 | 152.1933 | 29.0668 | 1744.0062 | Low
4 | 220 | 16.5285 | 145.5762 | 27.803 | 1668.1799 | Low
4 | 210 | 15.7772 | 138.9591 | 26.5392 | 1592.3535 | Low
4 | 200 | 15.0259 | 132.342 | 25.2755 | 1516.5271 | Low
4 | 190 | 14.2746 | 125.7249 | 24.0117 | 1440.7008 | Low
4 | 180 | 13.5233 | 119.1078 | 22.7479 | 1364.8744 | Low
3 | 120 | 9.0155 | 79.4052 | 26.9605 | 1617.629
3 | 115 | 8.6399 | 76.0966 | 25.8371 | 1550.2277
3 | 110 | 8.2642 | 72.7881 | 24.7138 | 1482.8265
3 | 105 | 7.8886 | 69.4795 | 23.5904 | 1415.4253
3 | 100 | 7.5129 | 66.171 | 22.4671 | 1348.0241
3 | 95 | 7.1373 | 62.8624 | 21.3437 | 1280.6229
3 | 90 | 6.7616 | 59.5539 | 20.2204 | 1213.2217
3 | 85 | 6.386 | 56.2453 | 19.097 | 1145.8205 | Low
3 | 80 | 6.0104 | 52.9368 | 17.9737 | 1078.4193 | Low
3 | 75 | 5.6347 | 49.6282 | 16.8503 | 1011.0181 | Low
3 | 70 | 5.2591 | 46.3197 | 15.7269 | 943.6169 | Low
2 | 54 | 4.057 | 35.7323 | 27.2975 | 1637.8493
2 | 52 | 3.9067 | 34.4089 | 26.2865 | 1577.1882
2 | 50 | 3.7565 | 33.0855 | 25.2755 | 1516.5271
2 | 48 | 3.6062 | 31.7621 | 24.2644 | 1455.8661
2 | 46 | 3.456 | 30.4387 | 23.2534 | 1395.205
2 | 44 | 3.3057 | 29.1152 | 22.2424 | 1334.5439
2 | 42 | 3.1554 | 27.7918 | 21.2314 | 1273.8828
2 | 40 | 3.0052 | 26.4684 | 20.2204 | 1213.2217
2 | 38 | 2.8549 | 25.145 | 19.2093 | 1152.5606 | Low
2 | 36 | 2.7047 | 23.8216 | 18.1983 | 1091.8995 | Low
2 | 34 | 2.5544 | 22.4981 | 17.1873 | 1031.2385 | Low
2 | 32 | 2.4041 | 21.1747 | 16.1763 | 970.5774 | Low
2 | 30 | 2.2539 | 19.8513 | 15.1653 | 909.9163 | Low
2 | 28 | 2.1036 | 18.5279 | 14.1543 | 849.2552 | Low
1 | 14 | 1.0518 | 9.2639 | 28.3085 | 1698.5104
1 | 12 | 0.90155 | 7.9405 | 24.2644 | 1455.8661
1 | 10 | 0.75129 | 6.6171 | 20.2204 | 1213.2217
1 | 8 | 0.60104 | 5.2937 | 16.1763 | 970.5774 | Low
1 | 6 | 0.45078 | 3.9703 | 12.1322 | 727.933 | Low
Note on G7: Hiran de Mel: The vast majority of systems utilizing centrifugal blowers are designed at pipe velocities of less than 3500 FPM which minimizes line losses and noise, with an accompanying decrease in power consumption.

## Fluid & Blower Information
AIR PROPERTIES: |  |  |  | BLOWER CHARACTERISTICS:
n = K-1/K = | 0.28672 |  |  | Efficiency = | 60% | https://www.engineeringtoolbox.com/air-specific-heat-various-pressures-d_1535.html
K = Cp/Cv = | 1.402
Cp = | 0.2403 | Btu/lbm-°R
Cv = | 0.1714 | Btu/lbm-°R
Gas Costant (R) = | R*/M = | 53.3479 | ft-lbf/lbm-°R
R* = | 1545.33 | ft-lbf/lbmol-°R
M = | 28.967 | lbm/lbmol
hd - hi = Cp(Td-Ti)
eff = (hdid - hi)/(hd - hi)
Specific Heat of dry air at constant temperature 20oC / 68°F at varying pressures:
[6 empty] | Pressure |  |  | Isobaric Specific Heat, Cp |  |  |  | Isochoric Specific Heat, Cv |  |  |  | Specific Heat Ratio
[6 empty] | [atm] | [psia] | [kPa] | [kJ/(kg K)] | [kWh/(kg K)] | [kcal/(kg °C)], | [kcal/(lb °F)] | [kJ/(kg K)] | [kWh/(kg K)] | [kcal/(kg °C)], | [kcal/(lb °F)] | Cp/Cv
[11 empty] | [Btu/(lb °F)] |  |  |  | [Btu/(lb °F)]
[6 empty] | 0.01 | 0.147 | 1.0132 | 1.0045 | 0.00027903 | 0.2399 | 0.1959 | 0.7174 | 0.00019928 | 0.1713 | 0.1399 | 1.4002
[6 empty] | 0.1 | 1.47 | 10.1325 | 1.0049 | 0.00027914 | 0.24 | 0.196 | 0.71763 | 0.00019934 | 0.1714 | 0.1399 | 1.4003
[6 empty] | 0.4 | 5.88 | 40.53 | 1.0053 | 0.00027925 | 0.2401 | 0.196 | 0.71766 | 0.00019935 | 0.1714 | 0.14 | 1.4008
[6 empty] | 11) | 14.7 | 101.325 | 1.0061 | 0.00027947 | 0.2403 | 0.1962 | 0.71767 | 0.00019935 | 0.1714 | 0.14 | 1.4019
[6 empty] | 7 | 102.9 | 709.28 | 1.0162 | 0.00028228 | 0.2427 | 0.1982 | 0.71913 | 0.00019976 | 0.1718 | 0.1402 | 1.4131
[6 empty] | 10 | 147 | 1013.25 | 1.0216 | 0.00028378 | 0.244 | 0.1992 | 0.72005 | 0.00020001 | 0.172 | 0.1404 | 1.4188
[6 empty] | 40 | 588 | 4053 | 1.0756 | 0.00029878 | 0.2569 | 0.2098 | 0.72858 | 0.00020238 | 0.174 | 0.1421 | 1.4763
[6 empty] | 70 | 1029 | 7092.8 | 1.1305 | 0.00031403 | 0.27 | 0.2205 | 0.73778 | 0.00020494 | 0.1762 | 0.1439 | 1.5323
[6 empty] | 100 | 1470 | 10132.5 | 1.1824 | 0.00032845 | 0.2824 | 0.2306 | 0.74703 | 0.00020751 | 0.1784 | 0.1457 | 1.5828
1) Standard atmosphere
Note on G2: Hiran de Mel: (Usually between 60% and 80%)

## Power Efficiency Calculator
|  | Blower #1 (rated) | [5 empty] | Aeration Control System Design -- Thomas E. Jenkins | U.S. DOE Energy Efficiency & Renewable Energy – Motor Systems Tip Sheet #11: Adjustable Speed Drive Part-Load Efficiency
Parameter (unit) | Symbol | Guaranteed | Tested | Specified | Adjusted | Example | Example
Flow (SCFM) | Qs | 5000 | 4389 | 4389 | 5000 | 7000 | 360
Specific weight of air at standard conditions (lbf/ft3) | γ | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075
Gas constant for air (ft.lbf/(lbm.°R) | R | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3
Blower inlet air temperature (°R) -- (°R = °F + 459.67) | Ti | 527.67 | 526.07 | 527.67 | 527.67 | 559.67 | 519.67
Ratio of specific heats for air (Cp/Cv = 1.395) | k | 1.395 | 1.395 | 1.395 | 1.395 | 1.395 | 1.395
| k-1/k | 0.28315 | 0.28315 | 0.28315 | 0.28315 | 0.28315 | 0.28315
Blower efficiency (decimal) | ηb | 0.72306 | 0.85247 | 0.85199 | 0.85786 | 0.8 | 0.7
Blower discharge pressure (psia) -- (psia = psig + barometric pressure) | Pd | 18.7 | 19.32 | 19.37 | 18.7 | 24.4 | 23.1692
Blower inlet pressure (psia) -- (psia = - inlet losses + barometric pressure) | Pi | 14.7 | 14.648 | 14.7 | 14.7 | 13.9 | 14.6
Barometric Pressure (psia) | Pamb | 14.7 | 14.7 | 14.7 | 14.7 | 14.4 | 14.7
Blower shaft power (bhp) | Pb | 110.0894 | 94.4846 | 94.4837 | 92.7912 | 361.8631 | 15.9723
Wire power, kW | P | 90.9991 | 78.1003 | 78.0996 | 76.7005 | 299.1134 | 13.2026
Wire to air efficiency (decimal) | ηwa | 0.65256 | 0.76935 | 0.76892 | 0.77422 | 0.722 | 0.63175
Efficiency of motor (decimal) | ηm | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
Efficiency of variable frequency drive if used, (decimal) | ηvfd | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
Lone Star Blowers
Legend
| 5000 | Input values
| 0.8 | Assumed input
| 82 | Calculated